## STATUS_DEFS
| BITS 0 to 7 DECIMAL | BITS 0 to 7 HEX
STATUS_ERR_PHASE_SEQUENCE | 0 | 00
STATUS_ERR_U1 | 1 | 01
STATUS_ERR_U2 | 2 | 02
STATUS_ERR_U3 | 3 | 03
STATUS_ERR_MAX_POWER | 4 | 04
STATUS_ERR_MAX_CURRENT | 5 | 05
STATUS_ERR_MIN_PHI | 6 | 06
STATUS_ERR_MIN_POWER | 7 | 07
STATUS_ERR_PHASE_IMBALANCE | 8 | 08
STATUS_ERR_AUX_INHIBIT | 9 | 09
STATUS_ERR_NO_CURRENT | 10 | 0A
STATUS_ERR_CONTROLLER | 11 | 0B
STATUS_ERR_MAX_STARTS | 12 | 0C
STATUS_ERR_SUPPLY_FREQ | 13 | 0D
STATUS_ERR_INSULATION | 14 | 0E
STATUS_ERR_BACK_EMF | 15 | 0F
STATUS_UNMAPPED_ERR | 16 | 10
STATUS_UNKNOWN | 100 | 64
STATUS_RUNNING | 101 | 65
STATUS_UNCALIBRATED | 102 | 66
STATUS_CALIBRATING | 103 | 67
STATUS_CAL_PAUSED_AUX | 104 | 68
STATUS_CAL_PAUSED_RST | 105 | 69
STATUS_RESET_ACTIVE | 106 | 6A
STATUS_CAL_PAUSED_MONO | 107 | 6B
STATUS_MONO_STARTUP | 108 | 6C
STATUS_STARTING | 127 | 7F

## STATUS_SPECIFIC_FRAME_DEFS
|  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
BYTE 0 | BYTE 0 | BYTE 1 | BYTE 2 | BYTE 3 | BYTE 4 | BYTE 5 | BYTE 6 | BYTE 7 | BYTE 8 | BYTE 9 |  |  |  | Max LEN of column N messages: 90
HEX | STATUS | TIME IN STATUS | Ad Info B0 | Ad Info B1 | Ad Info B2 | Ad Info B3 | Ad Info B4 | Ad Info B5 | Ad Info B6 | Ad Info B7 | Content of Error Message in Mobile App | Troubleshoot Guidelines | Telegram phase 1 Status message | LEN of column N message
00 | STATUS_ERR_PHASE_SEQUENCE | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Supply Voltage Sequence Incorrect" | Swap L1 and L2 on supply side. Then also check pump turning direction and if reversed, swap T1 and T2 on the contactor. | Supply voltage sequence incorrect. Swap L1 and L2. | 50
01 | STATUS_ERR_U1 | TIME IN STATUS | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l1_voltage | ms_controller. live_measurements. l2_voltage | ms_controller. live_measurements. l3_voltage | N/A | N/A | N/A | N/A | "Phase 1 Voltage Error. V1 = <meas v1>, V2 = <meas v2>, V3 = <meas v3> [Vpn] " |  | Supply voltage (L1) out of safe operational range | 49
02 | STATUS_ERR_U2 | TIME IN STATUS | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l1_voltage | ms_controller. live_measurements. l2_voltage | ms_controller. live_measurements. l3_voltage | N/A | N/A | N/A | N/A | "Phase 2 Voltage Error. V1 = <meas v1>, V2 = <meas v2>, V3 = <meas v3> [Vpn] " |  | Supply voltage (L2) out of safe operational range | 49
03 | STATUS_ERR_U3 | TIME IN STATUS | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l1_voltage | ms_controller. live_measurements. l2_voltage | ms_controller. live_measurements. l3_voltage | N/A | N/A | N/A | N/A | "Phase 3 Voltage Error. V1 = <meas v1>, V2 = <meas v2>, V3 = <meas v3> [Vpn] " |  | Supply voltage (L3) out of safe operational range | 49
04 | STATUS_ERR_MAX_POWER | TIME IN STATUS | ms_controller. protection_limits. limits_binary_exponents | ms_controller. protection_limits. power_high_limit | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l3_measured_power | ms_controller. live_measurements. l3_current | N/A | N/A | N/A | "Overload (Power). Power = <meas p3> [<engineering Watt unit: Watt or kW or MW>], High Limit = <p3 high limit> [<engineering Watt unit: Watt or kW or MW>], Current = <meas i3> [Amp]" |  | Overload (kW) | 13
05 | STATUS_ERR_MAX_CURRENT | TIME IN STATUS | ms_controller. protection_limits. limits_binary_exponents | ms_controller. protection_limits. current_high_limit | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l1_voltage | ms_controller. live_measurements. l2_voltage | ms_controller. live_measurements. l3_voltage | ms_controller. live_measurements. l3_current | N/A | "Maximum Current. Current = <calc i3>, Limit = <calc i_limit> [Amp], V1 = <meas v1>, V2 = <meas v2>, V3 = <meas v3> [Vpn] " |  | Maximum current (Amps) | 22
06 | STATUS_ERR_MIN_PHI | TIME IN STATUS | ms_controller. protection_limits. min_phi_limit |  | ms_controller. live_measurements. l3_phi |  | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l1_voltage | ms_controller. live_measurements. l2_voltage | ms_controller. live_measurements. l3_voltage | "Overload (Phase Angle). Phi = <meas phi>°, Phi Lim = <phi lim>°, V1 = <meas v1>, V2 = <meas v2>, V3 = <meas v3> [Vpn]" |  | Overload (phase angle) | 22
07 | STATUS_ERR_MIN_POWER | TIME IN STATUS | ad_info | ad_info == 0: ms_controller. protection_limits. limits_binary_exponents ad_info == 1: ms_controller. protection_limits. general_info | ad_info == 0: ms_controller. protection_limits. power_low_limit ad_info == 1: ms_controller. protection_limits. general_info (continued) | ad_info == 0: ms_controller. live_measurements. measured_binary_exponents ad_info == 1: ms_controller. live_measurements. l3_phi | ad_info == 0: ms_controller. live_measurements. l3_measured_power ad_info == 1: ms_controller. live_measurements. l3_phi (continued) | ad_info == 0: ms_controller. protection_timers. underload_restart_delay ad_info == 1: N/A | ad_info == 0: ms_controller. protection_timers. underload_restart_delay (continued) ad_info == 1: N/A | N/A | <if ad_info==0> "Underload. Power = <meas p3> [<engineering Watt unit: Watt or kW or MW>], Power Low Limit = <p3 low limit> [<engineering Watt unit: Watt or kW or MW>], Remaining Recovery Time = <restart_delay - time_in_status (converted to minutes)> [minutes]" <if ad_info==1> "Phase angle too big at calibration. Phi Max = <ct_position==internal?'80°':'60°'>, Phi Measured = <phi_meas>°" |  | Underload (kW) | 14
08 | STATUS_ERR_PHASE_IMBALANCE | TIME IN STATUS | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l1_voltage | ms_controller. live_measurements. l2_voltage | ms_controller. live_measurements. l3_voltage | N/A | N/A | N/A | N/A | "Phase Imbalance. V1 = <meas v1>, V2 = <meas v2>, V3 = <meas v3> [Vpn]" |  | Phase imbalance | 16
09 | STATUS_ERR_AUX_INHIBIT | TIME IN STATUS | ms_controller. protection_limits. aux_input | ms_controller. live_measurements. aux_input_status | N/A | N/A | N/A | N/A | N/A | N/A | "Auxilliary Inhibit. Configured as: <prot_lim.aux>, Status = <live_meas.aux>" |  | Auxiliary inhibit | 17
0A | STATUS_ERR_NO_CURRENT | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "No Current" |  | No current | 10
0B | STATUS_ERR_CONTROLLER | TIME IN STATUS | controller_error_number | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Controller Error Number <controller_error_number>" | "Check for any loose wires on the connectors of the controller" | Controller error | 16
0C | STATUS_ERR_MAX_STARTS | TIME IN STATUS | ms_controller. protection_limits. general_info |  | setting | minutes_until_restart | N/A | N/A | N/A | N/A | "Overheat Protection. Wait <setting> minutes. <minutes_until_restart> minutes remaining until restart." |  | Overheat protection | 19
0D | STATUS_ERR_SUPPLY_FREQ | TIME IN STATUS | ms_controller. live_measurements. Frequency | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Supply Frequency out of bounds. <f>0?'Freq = f [Hz]':' '>" |  | Supply frequency out of bounds | 30
0E | STATUS_ERR_INSULATION | TIME IN STATUS | insulation_fail_state | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Insulation Error. Failed at: <ifs==0?'Pre-Run Test': ifs==1?'Self-Test Active': ifs==2?'Self-Test Inactive': ifs==3?'Continuous Test': ifs==4?'Idle': 'Unknown'> " |  | Motor insulation error | 22
0F | STATUS_ERR_BACK_EMF | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Motor can not start." | "Check RUN, START and COM motor leads. Check RUN and START capacitors." | Motor can not start | 19
65 | STATUS_RUNNING | TIME IN STATUS | ms_controller. protection_limits. limits_binary_exponents | ms_controller. protection_limits. power_high_limit | ms_controller. protection_limits. power_low_limit | ms_controller. live_measurements. measured_binary_exponents | ms_controller. live_measurements. l3_measured_power | N/A | N/A | N/A | "Motor Running. Power Low Limit = <low limit>[<engineering Watt unit: Watt or kW or MW>], Measured Power = <p3 meas> [<engineering Watt unit: Watt or kW or MW>], Power High Limit = <p3 high limit> [<engineering Watt unit: Watt or kW or MW>]" |  | Motor running | 13
66 | STATUS_UNCALIBRATED | TIME IN STATUS | Valid Calibraion Method flags (1 = Valid, 0=Invalid): bit 0: Button bit 1: Prog Frame bit 2: Rem Req bit 3: Assisted Calibration bits 4 to 7: RFU | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Uncalibrated" |  | Uncalibrated | 12
67 | STATUS_CALIBRATING | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Busy Calibrating" |  | Busy calibrating | 16
68 | STATUS_CAL_PAUSED_AUX | TIME IN STATUS | ms_controller. protection_limits. aux_input | ms_controller. live_measurements. aux_input_status | N/A | N/A | N/A | N/A | N/A | N/A | "Calibration Paused by Auxiliary. Auxiliary input is configured as: <prot_lim.aux>, Status = <live_meas.aux>" |  | Calibration paused by auxiliary inhibit | 39
69 | STATUS_CAL_PAUSED_RST | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Calibration Paused by Reset." |  | Calibration paused by reset input | 33
6A | STATUS_RESET_ACTIVE | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "RESET INPUT ACTIVE! Protection stopped." |  | Reset input active. Protection paused. | 39
7F | STATUS_STARTING | TIME IN STATUS | ms_controller. protection_timers. t_start | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Motor is starting up. Startup expected to complete in: <t_start - time_in_status> [sec] |  | Motor is starting up | 20
64 | STATUS_UNKNOWN | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "The status of the Motorscope Device is UNKNOWN since NO DATA has been received from it yet." |  | The status of the Motorscope Device is UNKNOWN since NO DATA has been received from it yet | 90
10 | STATUS_UNMAPPED_ERR | TIME IN STATUS | ind_error | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Active Individual Error <ind_error>" |  | Motor stopped | 13
6B | STATUS_CAL_PAUSED_MONO | TIME IN STATUS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | "Calibration Paused by the MONO start-up delay" |  | Calibration paused by positive displacement pump start-up delay | 63
6C | STATUS_MONO_STARTUP | TIME IN STATUS | ms_controller. protection_timers. startup_underload_allow |  | N/A | N/A | N/A | N/A | N/A | N/A | "Mono Startup. Underload Error Suppressed until Startup Time expires in <startup_underload_allow - time_in_status> [sec]" |  | Positive displacement pump start-up delay | 41

## BIN_EXP,PWR,V,I
RANGE VALUE | PwrIncr | PwrMax | Vinc | Vmax | Iinc | Imax
0 | 1 | 255 | 2 | 510 | 0.0625 | 15.9375
1 | 2 | 510 | 4 | 1020 | 0.125 | 31.875
2 | 4 | 1020 |  |  | 0.25 | 63.75
3 | 8 | 2040 |  |  | 0.5 | 127.5
4 | 16 | 4080 |  |  | 1 | 255
5 | 32 | 8160 |  |  | 2 | 510
6 | 64 | 16320 |  |  | 4 | 1020
7 | 128 | 32640 |  |  | 8 | 2040
8 | 256 | 65280
9 | 512 | 130560
10 | 1024 | 261120
11 | 2048 | 522240
12 | 4096 | 1044480
13 | 8192 | 2088960
14 | 16384 | 4177920
15 | 32768 | 8355840
| DECODING |  |  |  |  | BIN EXP OCTET ENCODING
| HEX BIN EXP | PWR | V | I |  |  | Range Values (0:7)
| EF | 14 | 1 | 7 |  |  | Power (7:4) | V (3) | I (2:0)
| INCREMENT | 16384 | 4 | 8 |  | Value | 3 | 0 | 0
| MAX | 4177920 | 1020 | 2040 |  | BIN | 0011 | 0 | 000
[6 empty] | Incr | 8 | 2 | 0.0625
| HEX PWR | CALCULATED POWER [Watt] |  |  |  | Sat | 2040 | 510 | 15.9375
| 4E | 1277952 |  |  |  | HEX BIN EXP | 30
| HEX V | CALCULATED VOLTAGE [Vphase to neutral]
| c7 | 796
| HEX CURRENT | CALCULATED CURRENT [Amps]
| e3 | 1816

## GEN_INFO
GENERAL INFO BLE DECODE
| HEX BIG ENDIAN | FF05 |  | RESERVED | MIN PHI MONITORED | THREE MEASURED VOLTAGES | TWO MEASURED CURRENTS | OVERHEAT PROT METHOD | LOAD TYPE | CT POSITION | CT CORE MATERIAL | CT SECONDARY SIDE AMP RATING | CT PRIMARY SIDE AMP RATING
| BINARY LITTLE ENDIAN | 0000010111111111 |  | RFU | NO | NO | NO | MAX STARTS PER HOUR | STANDARD | EXTERNAL | MAGNETIC | 1 | 60
FIELD # | FIELD NAME | FIELD BINARY VAL | FIELD DESCRIPTIVE VAL | RFU | YES | YES | YES | PTC THERMISTOR | PD | INTERNAL | AIR | 5 | 75
0 | RESERVED | 1 | RFU |  |  |  |  | I2T | COMPRESSOR |  |  |  | 80
1 | MIN PHI MONITORED | 1 | YES |  |  |  |  | RFU | RFU |  |  |  | 100
2 | THREE MEASURED VOLTAGES | 1 | YES | [9 empty] | 125
3 | TWO MEASURED CURRENTS | 1 | YES | [9 empty] | 150
4 | OVERHEAT PROT METHOD | 11 | RFU | [9 empty] | 175
5 | LOAD TYPE | 11 | RFU | [9 empty] | 200
6 | CT POSITION | 0 | EXTERNAL | [9 empty] | 250
7 | CT CORE MATERIAL | 1 | AIR | [9 empty] | 300
8 | CT SECONDARY SIDE AMP RATING | 0 | 1 | [9 empty] | 400
9 | CT PRIMARY SIDE AMP RATING | 00000 | 60 | [9 empty] | 500
600
GENERAL INFO BLE ENCODE | [12 empty] | 750
| HEX BIG ENDIAN | 0440 | [10 empty] | 800
| BINARY LITTLE ENDIAN | 0100000000000100 | [10 empty] | 1000
FIELD # | FIELD NAME | FIELD DESCRIPTIVE VAL | FIELD BINARY VAL | [9 empty] | 1200
0 | RESERVED | RFU | 0 | [9 empty] | 1250
1 | MIN PHI MONITORED | NO | 0 | [9 empty] | 1500
2 | THREE MEASURED VOLTAGES | YES | 1 | [9 empty] | 1600
3 | TWO MEASURED CURRENTS | NO | 0 | [9 empty] | 2000
4 | OVERHEAT PROT METHOD | MAX STARTS PER HOUR | 00 | [9 empty] | 2500
5 | LOAD TYPE | STANDARD | 00 | [9 empty] | 3000
6 | CT POSITION | EXTERNAL | 0 | [9 empty] | 4000
7 | CT CORE MATERIAL | MAGNETIC | 0 | [9 empty] | RFU
8 | CT SECONDARY SIDE AMP RATING | 1 | 0 | [9 empty] | RFU
9 | CT PRIMARY SIDE AMP RATING | 250 | 01000 | [9 empty] | RFU
RFU
RFU
RFU
RFU
RFU

## TIME_IN_STATUS
[6 empty] | TIME IN STATUS VALUE | SECONDS INCREMENT | ACCUMULATED SECONDS
DECODE |  |  |  |  | TIME_IN_STATUS_INCR_IS_1SEC | 0 | 1 | 0 | 000000
HEX | ef |  | Time In Status | 38 | TIME_IN_STATUS_INCR_IS_1MIN | 60 | 60 | 59 | 00003B
DEC | 239 |  | Time In Status Index | 1 | TIME_IN_STATUS_INCR_IS_15MIN | 120 | 900 | 3599 | 000E0F
|  |  | Time In Status Seconds | 38 | TIME_IN_STATUS_INCR_IS_1HR | 240 | 3600 | 110699 | 01B06B
LOOKUP ROW PRELIM | 2 |  |  |  | TIME_IN_STATUS_INCR_IS_2HRS | 250 | 7200 | 143099 | 022EFB
TOTAL SECONDS IN STATUS | 111599 |  |  |  | TIME_IN_STATUS_MORE_THAN_2_DAYS | 255 | 7200 | 171899 | 029F7B
CORRESPONDING SECONDS
DAYS | 1 | 86400
HOURS | 6 | 21600 |  |  | NUM SECONDS PER DAY | 86400
MINUTES | 59 | 3540 |  |  | NUM SECONDS PER HOUR | 3600
SECONDS | 59 | 59 |  |  | NUM SECONDS PER MINUTE | 60